## Slide 1
Energy Program - 2014

## Slide 2
Program Goals
Practice good stewardship of public resources
Avoid wasting energy… Energy is money
Apply savings to fund improvements for more savings
Public Affairs is our mission … Set the example!

## Slide 3
Electricity
  Provider: City Utilities
Steam
  Provider: MSU Steam Generation Plant
  Uses: Heating: 24 buildings & Rec Ctr pool
Showers: Res Life, Athletics, Rec Ctr
Steam lines: Dining Halls
Hot water: Restrooms
Water
  Provider: City Utilities
Chilled Water Loop
  Provider: MSU Utilities
  Capacity: 5,930 tons
Utilities Distribution Tunnel
  1.75 miles underground tunnel system
Utilities Data

## Slide 4
Chart: Utilities (Cost Allocation)
| Electric $4,539,608 | Natural Gas $1,484,017 | Water $330,009 | Sewer $201,193
 | 4539608 | 1484017 | 330009 | 201193

## Slide 5
History of Energy Initiatives
1996-2014

## Slide 6
1996 Energy Project
History of Energy Initiatives
1996-2014

## Slide 7: High Energy Usage (1994)
129,075
95,167
171,610
Missouri
State
University
BTU/Sq Ft/Year
80% Above Regional
33% Above National
Regional
Avg
National
Avg

## Slide 8
Feasibility Study Revealed
  No centralized control of occupied buildings
  Inefficient lighting
  No sub-metering to manage high energy use
  Energy waste: $60K-$80K/mo
1996 Energy Review

## Slide 9
Solution Option: “Energy Performance Contract”
  MSU borrows funds
  Install energy improvements
  Debt service paid with generated savings
  If “guarantee” not met, contractor must pay
Energy Performance Contract” Executed
  $5.5M of energy improvements
  Scope of work:
  15,000 Lighting retrofits
  Variable speed drive motors
  Electric Meters in all major buldings
  Central Energy Management System

## Slide 10
Central Energy Management System
Saves energy when buildings are unoccupied
  Occupied Mode 70-75 degrees
  Unoccupied Mode
    Drifts to 80 degrees (summer)
    60 degrees (winter)
    Buildings systems are not shut off

## Slide 11
Energy Project Executed
  $5.5M of energy improvements
  Scope of work:
  15,000 Lighting retrofits
  Variable speed drive motors
  Electrical meters for all major facilities
  Central Energy Management System
  Energy savings: approx. $1M/yr
  Paid off in October 2005 (7.3 years)
1996 Energy Project

## Slide 12
1996 Energy Project – $5.5M Energy Improvements
1998 Electrical Distributions System Testing
1999 Utility Master Plan
History of Energy Initiatives
1996-2014

## Slide 13
1999 Utility Master Plan
Recommendations:
  Upgrade the electrical spine for the future
  Combine building chillers to “satellite plants”
  Phase out inefficient steam-absorption chillers

## Slide 14
1996 Energy Project – $5.5M Energy Improvements
1998 Electrical Distributions System Testing
1999 Utility Master Plan
2000 Utility Tunnel Repairs
  - $5M Capital Appropriation
History of Energy Initiatives
1996-2014

## Slide 15
Utility Distribution Tunnel
Strong
Siceluff
Cheek
Temple
CARR
Student Union
Karls
Craig
Hill
Wells
Woods
Hutchens
Garst
Hammons
BLSH
JQH Arena
Hammons Stu Ctr
Ellis
Kemper Hall
Greenwood
Lab
Rec Center
McDonald Arena
Freudenberger
Meyer Library
Morris
Hall
King St. Annx
Forsythe
Athl.Ctr
Pummill
PH
Art Annex

## Slide 16
Utility Distribution Tunnel
Strong
Siceluff
Cheek
Temple
CARR
Student Union
Karls
Craig
Hill
Wells
Woods
Hutchens
Garst
Hammons
BLSH
JQH Arena
Hammons Stu Ctr
Ellis
Kemper Hall
Greenwood
Lab
Rec Center
McDonald Arena
Freudenberger
Meyer Library
Morris
Hall
King St. Annx
Forsythe
Athl.Ctr
Pummill
PH
Art Annex

## Slide 17
2000 Utility Tunnel Repairs
  Upgraded electrical systems
  Reduced line loss
  Corrected structural deficiencies
  Set us up for the next phase

## Slide 18
1996 Energy Project – $5.5M Energy Improvements
1998 Electrical Distributions System Testing
1999 Utility Master Plan
2000 Utility Tunnel Repairs
2002 Mechanical Upgrade to Hammons Student Center
2004 Energy Project - $10.9M Chilled Water Loop
History of Energy Initiatives
1996-2014

## Slide 19
2004 Energy Contract
Scope
  Chilled Water Loop
  Services 20 buildings
  Replaces 16 old and inefficient chillers
  Charged by large, efficient chillers
    5 new
    4 existing
Cost:
  $10.8M of energy improvements
  To pay back within 15 years

## Slide 20
Chilled Water Distribution
Strong
Siceluff
Cheek
Temple
Carrington
Student Union
Pummill
Karls
Craig
Hill
Wells
Freudenberger
Woods
Hutchens
Garst
Hammons
Powerhouse
Total Design Capacity= 4,130 T
720T
750T
840T
1,000T
500T
320T
Art Annex
Morris

## Slide 21
Chart: 
| JAN | FEB | MAR | APRIL | MAY | JUNE | JULY | AUG | SEPT | OCT | NOV | DEC
2004 Therms | 254000 | 249500 | 197670 | 179180 | 189620 | 218650 | 217890 | 222950 | 201210 | 192250 | 198980 | 244470
2006 Therms | 200550 | 198070 | 161680 | 103770 | 92860 | 71220 | 62250 | 65070 | 75290 | 118560 | 156520 | 189370
2004 Project - Impact on
Natural Gas Consumption

## Slide 22
#1 –
#2 –
#3 –
#4 –
#5 –
City Utilities
Top 10 Natural Gas Customers
Missouri State University
Dairy Farmers of America
Springfield Board of Education
Clariant LSM-Missouri
U.S. Medical Center
Willow Brook Foods, Inc.
Cox Health
Kraft, Inc.
Regal-Beloit Electric Motors
St. Johns Regional Health Center

## Slide 23
2004 City Utilities
Top 10 Natural Gas Customers
2006 City Utilities
Top 10 Natural Gas Customers
Customer # 6
Customer # 7
Customer # 8
Customer # 9
Customer # 10
Customer # 2
Customer # 1
Customer # 2
Customer # 3
Customer # 4
Missouri State University
Customer # 3
Customer # 4
Customer # 5

## Slide 24
1996 Energy Project – $5.5M Energy Improvements
1998 Electrical Distributions System Testing
1999 Utility Master Plan
2000 Utility Tunnel Repairs
2002 Mechanical Upgrade to Hammons Student Center
2004 Energy Project - $10.9M Chilled Water Loop
2006 Utility Study
History of Energy Initiatives
1996-2014

## Slide 25
Rationale for a Study
Last Utility Master Plan 1999
Landscape had changed
    Utility spine upgrades 2000-03
    Chilled Water Loop Installation 2006
    Energy costs skyrocketed
      Natural Gas rates increased 185%
      Electricity rates increased 47%

## Slide 26
Scope
Evaluate:
    Boiler House and Steam Distribution System
    Chiller Water System
      Building Systems

## Slide 27
2006 Utility Study Recommendations
Chilled Water Loop Expansion
Develop Sound Steam Distribution PM Program
Cost-Center Accounting of Utilities
Alternative Energy Options

## Slide 28
  Chilled Water Loop Expansion
Action Taken

## Slide 29
Chilled Water Distribution
Strong
Siceluff
Cheek
Temple
Carrington
Student Union
Pummill
Karls
Craig
Hill
Wells
Freudenberger
Woods
Hutchens
Garst
Hammons
Powerhouse
Blair Shannon
JQH Arena
Hammons Stu Ctr
Ellis
Kemper
Greenwood
Lab
Total Design Capacity= 5,030 T
900T

## Slide 30
  Chilled Water Loop Expansion
  Boiler House Modernization Project
    Upgraded two boilers
      Tubes, refractory, burners, skin
    Supervisory Controls and Data Acquisition (SCADA)
Action Taken
Boiler Interior

## Slide 31
Boiler House

## Slide 32
New Boiler

## Slide 33
Power House Condensate Tank

## Slide 34
New Condensate Pit

## Slide 35
Controls - 2007

## Slide 36
New Control Room

## Slide 37
  Chilled Water Loop Expansion
  Boiler House Modernization Project
  Replacement of Insulation and Steam Traps
    Potentially $250,000/yr savings
Action Taken

## Slide 38
Insulation Issues

## Slide 39
SteamTrap Issues

## Slide 40
  Chilled Water Loop Expansion
  Boiler House Modernization Project
  Replacement of Insulation and Steam Traps
    Potentially $250,000/yr savings
Chilled Water System Enhancements
    Install Pressure Independent Valves
Action Taken

## Slide 41
Building Pressure Independent Valves
… restore capacity
Chilled
Water Loop

## Slide 42
Pressure Independent Valve Installation
Cheek
Carrington
Pummill
Craig
Freudenberger
Hutchens
Garst
Hammons
Hammons Stu Ctr
Ellis
Kemper
Greenwood
Lab
Installations since 2009
Temple
Plaster Sports Complex
Union
Strong

## Slide 43
PIV Installation Benefits
Loop Capacity Recaptured
Therefore, no chiller required for the
Foster Family Recreation Center!
Temple
Hill
Craig
#Valves 10
Ton A/C Saved 50T
#Valves 6
Ton A/C Saved 50T
#Valves 17
Ton A/C Saved 300T
#Valves 7
Ton A/C Saved 50T
40 Valves
450T
Ellis
=
450 T

## Slide 44
Pressure Independent Valve Installation
Cheek
Carrington
Pummill
Craig
Freudenberger
Hutchens
Garst
Hammons
Hammons Stu Ctr
Ellis
Kemper
Greenwood
Lab
Recently Installed
Proposed Installations
Temple
Plaster Sports Complex
Union
Strong

## Slide 45
  Chilled Water Loop Expansion
  Boiler House Modernization Project
  Replacement of Insulation and Steam Traps
    Potentially $250,000/yr savings
Chilled Water System Enhancements
    Install Pressure Independent Valves
    Air & Dirt Separators
Action Taken

## Slide 46
Air & Dirt Separator

## Slide 47
Dirt Removed
Eliminates Contaminants
Air Removed
Makes Denser Water
This means…
cleaner coils
…better heat transfer
…less costly chiller run time
…more savings and less
maintenance
DIRT
AIR
…less chilled water
Air-Dirt Separator
Coil
Pipeline

## Slide 48
Dirt Removed
Eliminates Contaminants
Air Removed
Makes Denser Water
This means…
cleaner coils =
…better heat transfer
…less costly chiller run time
…more savings and less
maintenance
DIRT
AIR
…less chilled water
Air-Dirt Separator
Coil
Pipeline

## Slide 49
Air/Dirt Separators
Strong
Siceluff
Cheek
Temple
Carrington
Student Union
Pummill
Karls
Craig
Hill
Wells
Freudenberger
Woods
Hutchens
Garst
Hammons
Art Annex
Morris
BLSH
JQH Arena
Hammons Stu Ctr
Ellis
Kemp
Greenwood
Lab
Powerhouse
Installation since 2009

## Slide 50
History of Energy Initiatives
1996 Energy Project – $5.5M Energy Improvements
1998 Electrical Distributions System Testing
1999 Utility Master Plan
2000 Utility Tunnel Repairs
2002 Mechanical Upgrade to Hammons Student Ctr
2004 Energy Project - $10.9M Chilled Water Loop
2006 Utility Master Plan
2007 – 2013 Add’l Energy Conservation Measures

## Slide 51
Add’l Energy Conservation Measures
  Occupancy Sensors & Relamping via DNR
    2009 Campus-wide Occupancy Sensors
    2010 Campus-wide Relamping

## Slide 52
Add’l Energy Conservation Measures
  Occupancy Sensors & Relamping via DNR
    Sensors paid off in one year
  Moved Electrical Feed to reduce demand rates

## Slide 53
Add’l Energy Conservation Measures
  Occupancy Sensors & Relamping via DNR
    Sensors paid off in one year
  Moved Electrical Feed to reduce demand rates
  Boiler replacement to match summer load

## Slide 57
Add’l Energy Conservation Measures
  Occupancy Sensors & Relamping via DNR Loan
    Sensors paid off in one year
  Moved Electrical Feed to reduce demand rates
  Boiler replacement to match summer load
  CW Loop Improvements

## Slide 58
Chilled Water Distribution
Strong
Siceluff
Cheek
Temple
Carrington
Student Union
Pummill
Karls
Craig
Hill
Wells
Freudenberger
Woods
Hutchens
Garst
Hammons
Powerhouse
BLSH
JQH Arena
Hammons Stu Ctr
Ellis
Kemp
Greenwood
Lab
Rec Center
North-South CW Leg

## Slide 59
Chilled Water Distribution
Strong
Siceluff
Cheek
Temple
Carrington
Student Union
Pummill
Karls
Craig
Hill
Wells
Freudenberger
Woods
Hutchens
Garst
Hammons
Powerhouse
Blair Shannon
JQH Arena
Hammons
Stu Ctr
Ellis
Kemper
Greenwood
Lab
Total Design Capacity= 5,030 T
900T
Forsythe
Forsythe
Connects to CW Loop
Rec Center

## Slide 60
Chilled Water Distribution
Strong
Siceluff
Cheek
Temple
Carrington
Student Union
Pummill
Karls
Craig
Hill
Wells
Freudenberger
Woods
Hutchens
Garst
Hammons
Powerhouse
Blair Shannon
JQH Arena
Hammons
Stu Ctr
Ellis
Kemper
Greenwood
Lab
Total Design Capacity= 5,030 T
900T
Forsythe
HHPA
Wehr
Sunvilla
HHPA & Wehr Band Hall
Rec Center

## Slide 61
Chilled Water Distribution
Strong
Siceluff
Cheek
Temple
Carrington
Student Union
Pummill
Karls
Craig
Hill
Wells
Freudenberger
Woods
Hutchens
Garst
Hammons
Powerhouse
Blair Shannon
JQH Arena
Hammons
Stu Ctr
Ellis
Kemper
Greenwood
Lab
Total Design Capacity= 5,930 T
900T
Forsythe
HHPA
Wehr
Sunvilla
Meyer Library
Connects to CW Loop
Rec Center
Meyer Library

## Slide 62
Completed Initiatives
  Occupancy Sensors & Relamping via DNR Loan
    Sensors paid off in one year
  Moved Electrical Feed to reduce demand rates
  Boiler replacement to match summer load
  CW Loop additional leg
  Continued Replacement of PIVs
  Outdoor LED Lighting

## Slide 63
Installation of
LED Lights in
Visitor
Parking Lot
Before
After

## Slide 64
History of Energy Initiatives
1996 Energy Project – $5.5M Energy Improvements
1998 Electrical Distributions System Testing
1999 Utility Master Plan
2000 Utility Tunnel Repairs
2002 Mechanical Upgrade to Hammons Student Center
2004 Energy Project - $10.9M Chilled Water Loop
2006 Utility Master Plan
2007 – 2013 Add’l Energy Conservation Measures
2009 - 2014 Heating & Cooling Efficiencies

## Slide 65: Heating & Cooling Efficiencies
At the Power House
    Policy & PM Enforcement
  Matching Equipment to the Campus Demand
  A New Synergy in Energy Conservation

## Slide 68: Heating & Cooling Efficiencies
At the Power House
  Policy & PM Enforcement
  Matching Equipment to the Campus Demand
  A New Synergy in Energy Conservation
Utility Distribution through the Tunnels
  Cleaning up Past Sins

## Slide 69
Carrington
Tunnel
2008-Present
2008
Present

## Slide 70: Heating & Cooling Efficiencies
At the Power House
  Policy & PM Enforcement
  Matching Equipment to the Campus Demand
  A New Synergy in Energy Conservation
Utility Distribution through the Tunnels
  Cleaning up Past Sins
At the Building
  Improving Heat Transfer & Reducing Flow

## Slide 72
Benefits of Energy Improvements
1997-2014

## Slide 73
Electrical Consumption
Energy
Chart: Electrical Consumption (kWh)
| FY96 | FY97 | FY98 | FY99 | FY00 | FY01 | FY02 | FY03 | FY04 | FY05 | FY06 | FY07 | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14
Would have been (kWh) | 63289579 | 63289579 | 69276719.3317 | 75773018.4932 | 75422101.4444 | 75646355.3317 | 73743861.8475 | 71130205.9764 | 71467997.4122 | 69587096.6298 | 73410299.3119 | 78567625.5367 | 75438077.1587 | 73566528.7707 | 84672506.4058 | 90963047.5217 | 87920188.1594 | 90853213.5362 | 94424416.204
$ Would have been | 4094835.7613 | 2310069.6335 | 2757213.4294 | 2780869.7787 | 2986715.2172 | 3010724.9422 | 3288976.2384 | 3613414.4636 | 3744923.0644 | 4022134.1852 | 4000861.3125 | 4171940.916 | 4752598.861 | 5068733.8323 | 5842402.942 | 6276450.279 | 6066492.983 | 6268871.734 | 6109259.7284
$ Actual | 0 | 2310069.6335 | 1782580.4294 | 1806236.7787 | 2012082.2172 | 2036091.9422 | 2314343.2384 | 2638781.4636 | 2770290.0644 | 3047501.1852 | 3026228.3125 | 2863595.916 | 3319365.861 | 3602884.8323 | 4435065.942 | 4542000.279 | 4458400.983 | 4340602.734 | 4539608
Actual (kWh) | 63289579 | 44788453 | 49216261 | 50810157 | 51158089 | 51891104 | 51944517 | 52868131 | 52724934 | 55527125 | 53928360 | 52688347 | 52291507 | 64276318 | 65826091 | 64614507 | 62907286 | 70188172
Would have been

## Slide 74
Natural Gas Consumption
Chart: 
| FY96 | FY97 | FY98 | FY99 | FY00 | FY01 | FY02 | FY03 | FY04 | FY05 | FY06 | FY07 | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14
Would have been (therms) | 2800000 | 2900000 | 3029906 | 3387789 | 3405079 | 3720986 | 3647217 | 3669392 | 3533382 | 3363166 | 3371463 | 3371463 | 3371463 | 3371463 | 3405177.63 | 3473281.1826 | 3542746.8063 | 3542746.8063 | 3613601.7424
Actual (therms) | 2900000 | 2186049 | 2561141 | 2627852 | 2869601 | 2916212 | 3023672 | 2958373 | 2654541 | 2231399 | 1828118 | 1730495 | 1847506 | 2244168 | 2259276 | 1753017 | 2327377 | 2543086
Would have been
Actual

## Slide 75
Total Energy Savings
Chart: 
| FY94 | FY95 | FY96 | FY97 | FY98 | FY99 | FY00 | FY01 | FY02 | FY03 | FY04 | FY05 | FY06 | FY07 | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14
Utility Bill (Actual) | 4100000 | 2798900 | 2990499 | 3311589 | 4448792 | 3777941 | 4106647 | 4409865 | 4879828 | 5296263 | 5074485 | 5240069 | 5501774 | 4906643 | 5414317 | 5451215 | 5879309 | 6023625
Utility Bill (Would have been)2 | 4002220 | 4002220 | 4525163 | 4757645 | 4973579 | 5181920 | 5417127 | 5754504 | 5806651 | 5984541 | 5968110 | 6139190 | 6719848 | 7035983 | 7829324 | 8303110 | 8133686 | 8306065 | 8217797
Column1 | 4002220 | 0 | 522943 | 232482 | 215934 | 208341 | 235207 | 337377 | 52147 | 177890 | -16431 | 171080 | 580658 | 316135 | 793341 | 473786 | -169424 | 172379 | -88268
Column2 | 0 | 0 | 0.13066 | 0.051375 | 0.045387 | 0.04189 | 0.04539 | 0.06228 | 0.0090619 | 0.030636 | -0.0027456 | 0.028666 | 0.094582 | 0.047045 | 0.11275 | 0.060514 | -0.020405 | 0.021193 | -0.010627
Actual
Would have been
Baseline Year

## Slide 76
Utility (Energy) Expenditures
Chart: 
| FY97 | FY98 | FY99 | FY00 | FY01 | FY02 | FY03 | FY04 | FY05 | FY06 | FY07 | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14
Energy Cost | 2500000 | 2798900 | 2990499 | 3311589 | 4448792 | 3777941 | 4106647 | 4409865 | 4879828 | 5296263 | 5074485 | 5240069 | 5501774 | 4906643 | 5414317 | 5451215 | 5879309 | 6023625

## Slide 77
Chart: 
| 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014
 | 1679078 | 2145172 | 2178521 | 2178521 | 2354590 | 2367561 | 2367561 | 2483937 | 2483937 | 2483937 | 2489532 | 2859532 | 2928371 | 2958334 | 3079334 | 3117722 | 3148236 | 3115178 | 3168778 | 3336390
Academic Building Growth
Gross Square Footage, Springfield Campus
95% Increase From 1994
Wehr Band Hall, Taylor Health Addition, Forsythe
Strong Hall, Karls Addition
Physical Therapy, CDL, Student Union
Meyer Library Addition
Bear Park South
JVIC
Willow Brook
Bear Park North, J.D. Morris
Bond Ctr
McQueary, Greenwood
Plaster Ctr
Notes: Waiting on pic from Photographic services

## Slide 78
Chart: Electrical Rates
| FY97 | FY98 | FY99 | FY00 | FY01 | FY02 | FY03 | FY04 | FY05 | FY06 | FY07 | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14
$/kWh | 0.0361 | 0.0367 | 0.0371 | 0.0365 | 0.0398 | 0.0367 | 0.0396 | 0.0398 | 0.0446 | 0.0508 | 0.0524 | 0.0578 | 0.0545 | 0.0531 | 0.063 | 0.0689 | 0.069 | 0.0699

## Slide 79
Chart: Natural Gas Rates
| 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014
Therms | 0.336 | 0.3119 | 0.2677 | 0.344 | 0.6353 | 0.4341 | 0.4855 | 0.5643 | 0.681 | 0.9645 | 0.737 | 0.904 | 0.556 | 0.587 | 0.5619 | 0.5702 | 0.49 | 0.5835

## Slide 80
Increases Since 1994
Building Growth since 1994: 95% 1,710,127 sf
Utility Rate increases:
Natural Gas 91%
Electric 46%
“Plug Growth”… increase in:
              Computers
              Refrigerators
              Copiers
              Microwaves
              Vending Machines
              Cell phones
Campus population increase: 20%
  Additional heat load
  Increases in exterior door openings

## Slide 81
Energy Efficiencies
Chart: 
| 1994 | 1998 | 1999 | 2007 | 2010 | 2011 | 2012 | 2013 | 2014
 | 180.1372 | 126.0433 | 134.4675 | 106.3443 | 89.4402 | 90.3478 | 77.3699 | 82.2566 | 86.9352
Chart: 
| 1995 | 1996 | 1997 | 1998 | 1999 | 2000 | 2001 | 2002 | 2003 | 2004 | 2005 | 2006 | 2007 | 2008 | 2009 | 2010 | 2011 | 2012 | 2013 | 2014
 | 1679078 | 2145172 | 2178521 | 2178521 | 2354590 | 2367561 | 2367561 | 2483937 | 2483937 | 2483937 | 2489532 | 2859532 | 2928371 | 2958334 | 3079334 | 3117722 | 3148236 | 3115178 | 3168778
Campus Growth
kbtu/sf/year
Notes: Waiting on pic from Photographic services

## Slide 82
Utility Bill Savings
Chart: 
| FY96 | FY97 | FY98 | FY99 | FY00 | FY01 | FY02 | FY03 | FY04 | FY05 | FY06 | FY07 | FY08 | FY09 | FY10 | FY11 | FY12 | FY13 | FY14
Utility Bill (Actual) | 4100000 | 2798900 | 2990499 | 3311589 | 4448792 | 3777941 | 4106647 | 4409865 | 4879828 | 5296263 | 5074485 | 5240069 | 5501774 | 4906643 | 5414317 | 5451215 | 5879309 | 6023623
Utility Bill (Would have been) | 4002220 | 4002220 | 4525163 | 4757645 | 4973579 | 5181920 | 5417127 | 5754504 | 5806651 | 5984541 | 5968110 | 6139190 | 6719848 | 7035983 | 7829324 | 8303110 | 8133686 | 8306065 | 8217797
Actual

## Slide 83
Net Energy Savings
From 1997-2014:
Energy Costs Avoided: $ 32M
Net Savings: $ 12.3M !

## Slide 84
‘98
’07(est)
129,075
171,610
95,167
126,043
105,037
Missouri
State
University
BTU/Sq Ft/Year
87,000
Impact of Energy Initiatives
1994
94,480
Regional
Avg
1998
2007
2014
1994
2014
97,800
National
Avg
1994
2014

## Slide 85
Benefits Beyond Savings
University & Community Involvement
  The Sustainability Movement
    Board Initiatives
      Energy Sub-Committee

## Slide 86
      Members:
        Associate Director Fac Mgmt (Chair)
        Energy Manager
        Associate VP of AIS
        Sustainability Coordinator
        Students
          Sustainability Committee members
        Faculty
        City Public Works
        City Utilities
Energy Sub-Committee
to the Presidentially-Appointed Sustainability Committee

## Slide 87
Benefits Beyond Savings
University & Community Involvement
  The Sustainability Movement
    Board Initiatives
      Energy Sub-Committee
      Revolving Fund for new Energy Projects
    Environmentally-Friendly

## Slide 88
Environmental Impact
(1997 - 2014)
The volume could fill:
POLLUTION REDUCTION:
Carbon Dioxide: 293,827 Tons
Nitrous Oxide (Acid Rain): 784 Tons
Sulfur Dioxide: 667 Tons
49
Goodyear Blimps
21,765
Goodyear Blimps
58
Goodyear Blimps

## Slide 89
Benefits Beyond Savings
University & Community Involvement
  The Sustainability Movement
    Board Initiatives
      Energy Sub-Committee
      Revolving Fund for new Energy Projects
      Energy Audit
    Concern for the Environment
    Energy Awareness

## Slide 90
Energy Green Kiosk
TIPS TO SAVE:
Turn out the lights when departing
Adjust thermostat
Close windows during hot/cold seasons
Turn off computer when not in use
Space heaters off when unattended
Notes: Insert dashboard pic

## Slide 93
Building Efficiencies Forward
    LEED Buildings

## Slide 94: Darr Ag Learning Center

## Slide 95
University Recreation Center

## Slide 96
Building Efficiencies Forward
    LEED Buildings
    Class Consolidation

## Slide 104: Class Consolidation Project
Phase I: Summer 2013
  4 partially unoccupied buildings (evenings & weekends)
  Savings of $15,939
  Reduction of 161 metric tons of carbon dioxide equivalent
Phase II: Summer 2014
  9 totally or partially unoccupied buildings (evenings & weekends)
  Savings of $38,976 (Accumulated)
  Reduction of 384 metric tons of carbon dioxide equivalent
Phase III: All year, starting Fall 2015

## Slide 105
Future Opportunities
  Chilled Water Reset

## Slide 106
Chilled
Water Loop
42°

## Slide 107
Chilled
Water Loop
42°
44°

## Slide 108
Chilled
Water Loop
44°
46°

## Slide 109
Chilled
Water Loop
46°
48°

## Slide 110
Chilled
Water Loop
48°
50°

## Slide 111
Chilled
Water Loop
50°
52°

## Slide 112
Chilled
Water Loop
42°
52°

## Slide 113
Chilled
Water Loop
42°

## Slide 114
Future Opportunities
  Chilled Water Reset
  Additional PIV’s to 6 buildings
  Addition Air/Dirt Separators – 10 locations
  Chilled Water Study
    Connections to CW Loop
      Sunvilla Tower
      Occupational Therapy
      Welcome Center

## Slide 115
Chilled Water Distribution
Strong
Siceluff
Cheek
Temple
Carrington
Student Union
Pummill
Karls
Craig
Hill
Wells
Freudenberger
Woods
Hutchens
Garst
Hammons
Blair Shannon
JQH Arena
Hammons
Stu Ctr
Ellis
Kemper
Greenwood Lab
Forsythe
HHPA
Wehr
Sunvilla
Rec Center
Meyer Library
Welcome Center
Art Annex
Power
house
Total Design Capacity
5,930 T
750T
840T
840T
500T
320T
1000T
900T
900T
Glass
Track/Soccer
LaCrosse/
Field Hockey
V.Ball
Occup. Therapy
Existing
Funded Work
Future

## Slide 116
Future Opportunities
  Chilled Water Reset
  Addition PIV’s to 6 buildings
  Addition Air/Dirt Separators – 10 locations
  Chilled Water Study
    Connections to CW Loop
      Sunvilla Tower, Occupational Therapy, Welcome Center
  More re-lamping parking lots with LEDs

## Slide 117
Outdoor LED Installations map

## Slide 118
Future Opportunities
  Chilled Water Reset
  Addition PIV’s to 6 buildings
  Addition Air/Dirt Separators – 10 locations
  Chilled Water Study
    Connections to CW Loop
      Sunvilla Twr, Occup Therapy & Welcome Ctr
  More re-lamping parking lots with LEDs
  Virtual Servers
    Collaboration with Computer Services
  LEED EB (existing building)
  Photo-voltaics
  Solar heating
  Wireless Thermostats
  Continue to educate the campus community

## Slide 119: Class Consolidation- Emissions Reductions
81 cars/year
53 Home’s electricity use/year
315 acres of forests/year
384 metric tons of Carbon Dioxide Equivalent is similar to:

## Slide 120
Executing its
Public Affairs Mission
through Energy Conservation
Questions?