Sustainability proposal

Retrofit the existing 400 watt high pressure sodium (HPS) lighting system located in the Parking lot #15 to LED lighting system

Submitted by:

Bryce Shields

lauren bansbach

Submitted on:

11/13/2012

- Identification of Sponsors

  - Project Sponsors (insert project sponsors and contact information below)

1. 	Bryce Shields

Bryce929@live.missouristate.edu

(816) 383-3867

  - Faculty/Staff advisor (insert faculty/staff contact information below)

1.	Robert Eckels

Director, Facilities Management

901 South National Avenue

Springfield, MO 65897

(417) 836-6865

Johnnysponsor@missouristate.edu

  - Project Manager (identify manager below, could also be a project sponsor)

      - Bryce Shields

II. 	Description of Proposed Project

- General Description of Proposal

This proposal is recommending that the (16) 400 Watt High Pressure Sodium lights in parking lot #15 be replaced with light-emitting diode (LED) lighting system. With this conversion, there will be a reduction in energy usage of 43%, annual energy savings of $951, and an approximately annual maintenance savings of $1024 (86% reduction).

- Proposal Details

The following table outlines the major differences between the current system and the proposed LED system.

| Characteristic | 400W HPS Light | LED Light |
| --- | --- | --- |
| Photometric Performance | Low | High |
| Working life | Medium | High (>50,000 hours) |
| Power consumption (input) | 472 Watts | 270 Watts |
| Startup speed | Low | High (2 seconds) |
| Optical efficiency | Low | High |
| Color temperature | Low (yellow or amber) | High |
| Bad glare | High | No harmful glare |
| Light pollution | High | No |
| Environment pollution | High | No |
| Maintenance cost | High | Low |

The following table outlines the difference in current and proposed systems’ energy consumptions.

| 400 W HPS | 270 W LED |
| --- | --- |
| Quantity | 16 | 16 |
| Luminaire Power | 472 Watts | 270 Watts |
| Total power (for parking lot 15) | 7,552 Watts | 4,320 Watts |
| Hours/year (11.5 hours per day) | 4,200 | 4,200 |
| Energy used per year | 31,719 kWh | 18,144 kWh (57% reduction) |

- Proposed location for the object of the proposal

Parking lot # 15 is located at the Missouri State University campus, between the streets E. Harrison St., E. Monroe St. and MSU Driveway.

Area of the parking lot = 115,596 ft2

Dimensions: 338 ft (E/W); 342 ft (N/S)

Existing lights: 400 Watts High Pressure Sodium

CWA Ballast input = 472 Watts

Height of the light poles = 40 ft

Spacing between the light poles

86 ft (straight line parallel to Harrison St.)

94 ft (straight line parallel to J.Q. Hammons)

- Alternative Uses

The better lighting could act as a crime deterrent.

- Drawbacks

The initial investment may seem quite costly.

- Necessary modifications to existing structures

In order to install the selected LED lights (model GE Evolve LED EAMT) on the existing poles, a pole top tenon is required. The price of the pole adaptor is included on the first cost of the equipment (section II).

- Estimated Cost of the Project

  - Provisions of Alternatives in Order of Preference

| Item | Units | Grainger Quote | Lighting Solutions Quote |
| --- | --- | --- | --- |
| GE Evolve LED EAMT | 16 | $21,845.44 | $24,304.00 |
| Pole Top Tenon Adapter | 16 | $2,156.96 | $1416.00 |
| Approx. Installation cost | 16 | $2,080.00 | $2080.00 |
| Total First cost Total Cost (with 10% overage) | 16 | $26,082.40 $28,690.64 | $27,800.00 $30,580.00 |

  - Provisions of Complete Cost Breakdowns

| Item | 400 W HPS | 270 W LED |
| --- | --- | --- |
| First cost of system (Grainger quote) | - | $26,082.40 |
| Annual energy cost | $2221 | $1270 |
| Annual energy savings | - | $951 (43%) |
| Annual maintenance cost | $1184 | $160 |
| Annual maintenance savings | - | $1024 (86%) |
| Total annual savings | $1975 |

  - Provisions of any Ongoing

There should be no ongoing costs outside typical maintenance that is required regardless of the system.

- Estimated Completion Time of Project

After the project is approved and the order is placed, the delivery time will be 7 weeks. Shipping time is in the range of 2 weeks. After the lights are received, they can be installed between 2 and 3 days. Based on this information, this project can be completed in a range of 10 weeks.

- Estimated Life of Project (Once completed, how long will the project last?)

This specific model GE Evolve EAMT is rated at 50,000 hours (approx. 12 years), at a temperature range of -40C to 50C. This system will be installed with a photocell and it will work from sunset to sunrise (11.5 hours per day, 4200 hours per year).

- Justification of Project

This project will benefit the University community by lowering operation costs. The money that would otherwise be spent on energy can be funneled to other projects.

- University Support (if applicable) ( Signed letter(s), or email(s), of support from appropriate administrator(s), as necessary. The letter(s) of support should detail any ongoing commitments, maintenance, support, or costs associated with the proposal that will be assumed by the University.)

# Text boxes

Missouri State University

Student Government Association